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CHARGE SPECIFICATIONS�
�
Recommended Charge Current�
40 A�
�
Maximum Charge Current�
200 A�
�
Recommended Charge Voltage�
28.4 V – 29.2V�
�



BMS Charge Voltage Cut-Off�
29.2 V (3.65 ±0.025 v) (2 s)�
�
Reconnect Voltage�
28.0 V (3.5 ±0.05 v)�
�
Balancing Voltage�
27.2V (3.4 ±0.025 v)�
�



COMPLIANCE SPECIFICATIONS�
�



Certifications�
UN38.3 (battery) CE (battery)


UL1642 (cells)�
�
Shipping Classification�
UN 3480, CLASS 9�
�



DIMENSIONAL SPECIFICATIONS�
�
�
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ELECTRICAL SPECIFICATIONS�
�
Nominal Voltage�
25.6V�
�
Nominal Capacity�
200 Ah�
�
Capacity @ 40A�
300 min�
�



Resistance�



≤15 mΩ @ 50% SOC�
�
Efficiency�
98%�
�
Self Discharge�
<3% per Month�
�
Cycle Life�
4000 times DOD80% (0.5C)�
�
Maximum Modules in parallel�
2�
�



DISCHARGE SPECIFICATIONS�
�
Maximum Continuous Discharge Current�
200 A�
�
Peak Discharge Current�
700 A (3-5 s)�
�
BMS Discharge Current Cut-Off�
700 A (3-5 s)�
�
Recommended Low Voltage Disconnect�
21.6 V�
�
BMS Discharge Voltage Cut-Off�
20 V (2.5 ±0.08 v) (2s)�
�
Reconnect Voltage�
21.6 V (2.7 ±0.1 v)�
�
Short Circuit Protection�
200-600 µs�
�



TEMPERATURE SPECIFICATIONS�
�
Discharge Temperature�
-4 to 140 °F (-20 to 60 °C)�
�
Charge Temperature�
32 to 131 °F (0 to 55 °C)�
�
Storage Temperature�
14 to 113 °F (-10 to 45°C)�
�
BMS High Temperature Cut-Off�
167 °F (75 ºC)�
�
Reconnect Temperature�
122°F (50 ºC)�
�



MECHANICAL SPECIFICATIONS�
�



Dimensions (L x W x H)�
20.47 x 10.59 x 8.66 inch


520 x 269 x 220 mm�
�
Weight�
83.7 lbs (38.0 kg)�
�
Terminal Type�
M8 x 1.25�
�
Terminal Torque�
80 - 100 in-lbs (9 - 11 N-m)�
�
Case Material�
ABS�
�
Enclosure Protection�
IP65�
�
Cell Type�
LiFePO4�
�
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